North Dakota Lead Service Line Replacement Plan Guidance & Template (LSLR Plan)

All Community Water Systems (CWS) and Non-Transient Non-Community (NTNC) Water Systems with one or more Lead, galvanized requiring replacement (GRR) or Lead status unknown service lines within their distribution system must complete and submit to the North Dakota Department of Environmental Quality (NDDEQ) a Lead service line replacement (LSLR) plan no later than November 1, 2027. (40 CFR§141.80(a)(3)).

To assist PWSs, NDDEQ is providing this guidance document and template outlining the necessary elements for a complete LSLR Plan. All parts of this plan are required to be included as part of the application.

Included in this guidance document, is a template for the LSLR Plan, appendices with examples of LSLR Plan handouts/boiler plate forms and instructions for how and where to submit the LSLR Plan to NDDEQ

This template meets the requirements for an LSLR Plan in accordance with LCRI 40 CFR § 141.84 (a-i) Service Line Inventory & Replacement Requirements. The Lead and Copper Rule Improvements propose to require a LSLR Plan in 2027; however, NDDEQ requires that a LSLR Plan prior to November 1, 2027,and submit it to NDDEQ for approval. The purpose of the plan is to prepare PWS’s for the eventuality that a Lead service line (LSL) will need replacement, even if the replacement is not planned or scheduled.

This plan should be updated when new information becomes available regarding the replacements, identification of LSLs, changing priorities, contract expirations, or changes in staff. In addition, the LSLR Plan is required to be made publicly available, updated and resubmitted annually to NDDEQ.

Table of Contents

- General Information

- Plan Certification Signature Page

- Responsible Parties

- Service Line Inventory Development and Maintenance

- Replacement Schedule Development & Replacement Considerations

a.  Methods used to identify the prioritization of Lead service line replacements

b.  Explanation of how the system prioritizes replacement location & how the schedule will be

implemented.

c.  Laws/ Regulations for Access for Service Line Replacement

d.  Coordination with Property Owners

e.  Replacement of Service Line Strategy

f.   Disposal of Lead and GRR Service Lines

g.  Emergency Replacement

- Financing

  - Lead Service Line Replacement Financing (40CFR141.84(c)(1)(iv)

  - Setting Aside Funds for Mailing & Other Future Costs

- LSL Replacement Procedure (40CFR141.84(c)(1)(ii)&(iv)

  - Lead Service Line Replacement Map

- Consumer Notification Requirements (40CFR141.84(c)(vii & 141.84(h)(1-3)

- Lead Risk Mitigation Procedures

- Lead Service Line Replacement Goal Rate (40CFR141.84(d)(5-6)

  - Eligibility for Deferred Deadline for LSLR (40CFR141.84(d)(5)(vi)(A-C))

- Annual Reporting Requirements for LSLR Plan

- Appendices

  - Appendix A – Instruction for customer flushing following a Lead service replacement

    - Template 1 – Consumer Notice for Full or Partial LSL Replacement

    - Template 2 – Disturbance to a Known or Potential Service Line Containing Lead/ GRR

    - Template 3 – Disturbance to a Known or Potential Service Line Containing Lead due to Meter or Connector Change out.

    - Template 4 – Utility Notification of Intent to Replace Customer Portion of an LSL

    - Template 5 – Planned Lead Service Line Replacement Notification- Required to be sent 45 days prior to work starting

  - Appendix B – Flushing by utility /contractor immediately after Lead service replacement

  - Appendix C – NDDEQ Tracking Form-PWS Attempts to Contact Customers for LSL Replacement ( in development)

  - Appendix D – Consumer Service Line Material Type Notification Template

Lead Service Line Replacement Plan

[Insert Public Water System Name]

- General Information. PWS ID #: ______________________ PWS Class ☐ CWS ☐ NTNC Plan Submission Type ☐ Initial Plan ☐ Revised Plan Date of Submission 00/00/0000 Mailing Address Street/Mailing Address:___________________________________________________ City:___________________________________________________________________ Zip Code:_______________________________________________________________ General Contact Phone Number: xxx-xxx-xxxx.

2. Plan Certification Signature Page

*I have verified and certified the information listed in this plan is true and accurate to the best of my knowledge and belief and will be followed as required.

| System Owner/ City Mayor/ or System Executive Director |  |
| --- | --- |
| Name Signature: | Name Print: |
| Date: | Title: |
| PWS Public Works Director |  |
| Name Signature: | Name Print: |
| Date: | Title: |
| Plan Preparer |  |
| Name Signature: | Name Print: |
| Date: | Title: |

3. Responsible Parties

List names, titles, and details for the following:

- PWS contact person for funding questions for public:

- Public Outreach Coordinator:

- Maintaining the online inventory updates:

- Resubmission of the LSLR Plan:

4. Service Line Inventory Development and Maintenance

Strategy for identifying service lines of “Unknown” materials (40CFR§141.84(a-b) and 40CFR§141.84(c)(1)(i) must be identified. - Note: under LCRI all service lines must be identified by 2031 regardless of their composition material. Check all applicable boxes of the strategies that your PWS is using to develop their service line inventory and how they plan to identify the unknown service lines. If task is not completed leave date field empty. When completed, include completion date.

| Check Box | Type of Review | Completion Date Review |
| --- | --- | --- |
| ☐ | We do not have service lines of unknown material within our water system’s service area |  |
| ☐ | Review historical building records and plumbing codes |  |
| ☐ | County and municipal ordinances |  |
| ☐ | Field /visual inspection with or without full excavation |  |
| ☐ | Historical building records and permits on each service connection |  |
| ☐ | Distribution system maps and drawings |  |
| ☐ | Most recent approved Lead & Copper Rule material survey |  |
| ☐ | Ongoing updating of service line materials during normal operations |  |
| ☐ | Capital improvement plans, as-builts and/or master plans for distribution system development |  |
| ☐ | Utility records including meter installation records, customer complaint investigations and field activity records |  |
| ☐ | Utility construction standards, standard details, and standard operating procedures |  |
| ☐ | Other documentation which indicates and/or confirms the location of Lead service lines: description of documentation |  |
| ☐ | Community survey |  |
| ☐ | Contacts within the water system, municipal office, or other local officials |  |
| ☐ | Survey results from area plumbers |  |
| ☐ | Documented interviews of residents - letters, phone survey, personal contact, etc. |  |
| ☐ | Aerial map of PWS for developments after Lead ban |  |
| ☐ | Visual inspection |  |
| ☐ | Customer self-identification |  |
| ☐ | Sequential water sampling |  |
| ☐ | Scratch test of service lines |  |
| ☐ | Door to door field inspections of customer side of the service line |  |
| ☐ | Excavation – Vacuum |  |
| ☐ | Excavation – Mechanical |  |
| ☐ | Water quality sampling (specify protocol) |  |
| ☐ | Predictive modeling (Must have prior approval by NDDEQ) |  |
| ☐ | Other: (describe) |  |

5. Replacement Schedule Development & Replacement Considerations

5a. Prioritization of Service Line Replacement (40 CFR§141.84(c)(1)(v)) Please rate the priority level for each listed criteria if considered for replacement of Lead and/or GRR service lines. Mark not applicable if the criteria was not considered.

Low; Medium; High Priority; Not Applicable. Disadvantaged Consumers *; ☐; ☐; ☐; ☐. Known Lead service lines *; ☐; ☐; ☐; ☐. Sensitive Populations *; ☐; ☐; ☐; ☐. Proximity to high Lead results *; ☐; ☐; ☐; ☐. Previous partial replacement *; ☐; ☐; ☐; ☐. Areas that receive many water quality complaints *; ☐; ☐; ☐; ☐. Overburdened Communities *; ☐; ☐; ☐; ☐. Licensed Childcare Centers *; ☐; ☐; ☐; ☐. Areas with high density of children *; ☐; ☐; ☐; ☐. Areas where all service lines are of unknown material; ☐; ☐; ☐; ☐. Areas where pipe replacements are already being conducted; ☐; ☐; ☐; ☐. Previous participation in Lead & Copper sampling; ☐; ☐; ☐; ☐. Areas with no service lines of unknown material; ☐; ☐; ☐; ☐. Age of current water main; ☐; ☐; ☐; ☐. Proximity to other known contaminants; ☐; ☐; ☐; ☐. System pressure grade line; ☐; ☐; ☐; ☐. Ownership; ☐; ☐; ☐; ☐. LSLs close to interconnections with a wholesaler which utilizes corrosion control treatment; ☐; ☐; ☐; ☐. Areas of source water or treatment changes; ☐; ☐; ☐; ☐. Areas where all residents have agreed to participate in the program; ☐; ☐; ☐; ☐. Service lines containing Lead only on the water system; ☐; ☐; ☐; ☐. Service line containing Lead only on the property owner side; ☐; ☐; ☐; ☐. Predictive modeling results.; ☐; ☐; ☐; ☐. * Prioritization strategy must include, but is not limited to, known LSLs and LSLR for disadvantage consumers and sensitive populations. Infants, young children, and pregnant women are the most vulnerable to Lead exposure.

5b. Explanation of how the system prioritizes replacement locations using the methods identified above and how the schedule will be implemented. Example: The prioritization of the replacements is focused on identifying areas with sensitive populations such as daycares and preschools. Past sampling events have shown that these areas also have high Lead results. By focusing replacement on these areas first, we are addressing the areas where Lead contamination has the most adverse impact on the health of those who drink the water.

5c. Law/ Regulations for Access for Service Line Replacement. Identify any laws/policies/regulations that could affect the water system’s ability to gain access to conduct full replacement. - Attach law/policy to LSLR Plan.

5d. Coordination with Property Owners

What portion of the service line is owned by the PWS? ☐ The PWS owns the entire service line (main to house) ☐ The PWS owns a portion of the service line (main to curb stop or meter) ☐ The PWS does not own any portion of the service line

If the PWS, does not own the entire service line, will the PWS create an ordinance which mandates the replacement of all the Lead /GRR service lines regardless of ownership? ☐ Yes ☐ No Date of anticipated Ordinance going into effect: * Attach a copy of ordinance to the LSLR Plan.

How will the system conduct public outreach regarding its LSLR Plan? Provide links to all publicly available materials.

How will the system solicit property owner/customer’s approval to replace LSL?

Provide a summary of any legal requirements or anticipated obstacles. For example: prior to replacing the property-owner portion of a LSL, a contract between the water system, contractor and property-owner must be signed and executed through the following process.

In the event of a property owner/customer’s refusal to replace the service line, the water system will: ☐ Document the incident with signed & dated customer refusal form and maintain document for records. ☐Continue to make a reasonable effort to contact owner/customer at least four times for participation and document all outreach efforts. ☐ When applicable, inform the property owner/customer that they refuse to replace their portion of the LSL; therefore, the LSL in its entirety must remain. Note: To ensure that the PWS make sufficient effort at replacing the customer owned portion of the service line, PWS will track their communication attempts. PWS will track a minimum of four attempts by the applicable deadline for replacing the customer-owned portion of the service line, number of non-responses and refusals for each address, as well as the type and dates associated with these communication attempts. This is required information under the LCRI that must be provided to NDDEQ. *If there is a change in ownership the PWS must make reasonable efforts again. NDDEQ has provided a refusal and non-response tracking form, see Appendix C. ☐ Check this box indicating that the PWS will track communications attempts and refusals, either using the Department form or another system or electronic tracking method.

5e. Replacement of Service Lines Strategy

How do you plan to replace the Lead & GRR service lines? Select all that apply below. ☐ Boring ☐ Trenching ☐ Pipe pulling ☐ Other, Explain: PWS must provide a copy of their Standard Operating Procedure (SOP) document for conducting full and partial replacement of Lead & GRR service lines. Reference information can be found at: American Water Works Association handout: ANSI/AWWA C810-17 Replacement and Flushing of LSLs. Attach a copy of your PWS specific SOP document to the LSLR Plan.

5f. Disposal of Lead/GRR Service Lines

How will the water system take steps to make sure all LSLs removed are disposed of properly? ☐ By ensuring that the contractors remove them to an appropriate licensed/permitted facility/scrapyard for disposal. List of licensed scrapyards can be found at the following weblink https://deq.nd.gov/Publications/WM/ScrapMetalAndAutoRecyclersList.pdf - Note you cannot dispose of Lead or metal service lines at ND landfills. LSLs will be considered hazardous waste since they will not pass TCLP test for toxicity. ☐ By keeping records of the scrap sale ticket and receipts on file for your records. ☐ Lead/GRR service lines are abandoned in the ground: ☐ Yes ☐No If yes: Is the required paperwork filed with NDDEQ – Division of Waste Management *(We are currently working on developing this document with Waste Management) Refer to NDDEQ Water Service Line Disposal Requirements Memo for required paperwork at: (Insert Website for memo here when finalized)

5g. Emergency Replacement

What steps will the water system take in the event an emergency replacement is necessary? ☐ By having materials, staff resources, and procedures in place to replace the service line. ☐ By replacing the line as part of the emergency repair. ☐ By documenting the service line materials if they are made known and replaced at a later date. ☐ Other ____________________________________________________________________ ☐ List sampling and notification procedures that will be implemented during an emergency replacement: Insert list here:

6. Financing

6a. Lead Service Line Replacement Financing (40 CFR § 141.84(c)(1)(vi))

Will the water system need to have approval from another agency or governing body prior to beginning replacements (due to budgetary issues)? ☐ Yes ☐ No If yes, explain:

List financial approvals, (certifications/permits) if any, that will need to be obtained before beginning replacements:

How will replacements be funded: Which of the following funding streams will apply below? Check all that apply from the list below ☐ Water Rates ☐ Special Assessments ☐ Private grants other than SRF ☐ Other: Please explain “other” below: Is the water system government owned? ☐ Yes ☐ No - If yes, will the property owner be responsible for a portion of the replacement cost? ☐ Yes ☐ No - If yes, what amount?__________________________ How will the utility address customer owned portions of service lines that are owned by customers who are unable to pay to replace the portion they own? (40 CFR § 141.84(c)(1)(vi)) Explain. Does the water system intend to apply for financing through the Drinking Water State Revolving Fund (DWSRF)? ☐ Yes ☐ No

6b. Setting Aside Funds for Mailings and Other Future Costs Our water system will ensure that there are adequate funds to cover the cost of LSLR activities by (select all that apply):

☐ Securing and setting aside funds on a yearly basis to cover the additional costs of certified mailing associated with each phase of replacement. ☐ Securing and setting aside funds for any outreach costs associated with replacements. ☐ Securing and setting aside funds for customer samples following an LSLR. ☐ Securing and setting aside funds for filter pitchers and replacements provided following an LSL replacement. ☐ Making sure that there is adequate funding, set aside if additional staffing is needed. ☐ Securing and setting aside funds if additional LSLs and galvanized requiring replacement service lines are identified and must be replaced. ☐ Other – List below:

7. LSL Replacement Procedure 40 CFR § 141.84(c)(1)(ii) & (iv))

☐ We will comply with ANSI/AWWA C810-17 Replacement and Flushing of LSLs. ☐ We will use alternative procedures. (Attach documentation of procedure to LSLR Plan)

How do you plan to provide Lead-removal filters for your customers? Refer to EPA’s guidance on Lead-removal home devices handout (NSF-certified) at (https://www.epa.gov/system/files/documents/2024-06/how-to-id-filters-certified-to-reduce-Lead-in-drinking-water-epa_june-2024.pdf For customers with identified LSLs prior to replacement, under a system-wide action level exceedance (ALE), these filters will be provided to: ☐ To all customers served by the PWS ☐ Household with known Lead/GRR service lines. ☐ To customer who requests them no matter what their service line material type What types of filters will be provided? ☐ POU device under the sink or whole house ☐ Pitcher Will additional replacement filters be provided? ☐ Yes ☐ No How will the replacement filters be provided/requested by the customers: Explain below Water testing is required for both SRF funding & under the LCRI after LSL replacement. Who will provide the customers with the water sample kit? Check all that apply: ☐ PWS operator ☐ Removal contractor ☐ 3rd party laboratories mail in/ request slips or coupons ☐ Other Explain below:

7a. Lead Service line Replacement Map

Lead service line replacement Map: Do you have a distribution map? ☐ Yes ☐ No Web link address of the map________________

8. Consumer Notification Requirements 40 CFR §141.84(c)(vii) and 141.84(h)(1-3)

☐ We will notify owner and non-owner customers of plans to conduct a full or partial service line replacement at least 45 days in advance (40 CFR § 141.84(h)(i) and 40 CFR§141.84(h)(2-3)): ☐ Using Template 5 form (Appendix A) ☐ Using our own template (PWS must provide example of the Template) ☐ We will use NDDEQ template letters for the following notifications (Appendix A) ☐ Public Education. ☐ Lead Risk Mitigation. ☐ Annual notifications of LSLs – each year customers who still have an LSL must receive a notification. ☐ Annual notifications of galvanized requiring replacement service lines – required every year. ☐ Annual notifications of service lines with unknown materials – required every year. ☐ We will use our own template letters for the following notifications - (PWS must provide example of all forms being used for handouts/ notification and all forms/handouts must be approved by NDDEQ) ☐ Public Education. ☐ Lead Risk Mitigation. ☐ Annual notifications of LSLs – each year customers who still have an LSL must receive a notification. ☐ Annual notifications of galvanized requiring replacement service lines – required every year. ☐ Annual notifications of service lines with unknown materials – required every year.

| 9. Lead Risk Mitigation Procedures |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| - The information below is to be used when certain handouts and pitcher filters must be provided to the customer by either the PWS or Contractor. - Templates can be found in Appendix A |  |  |  |  |  |
| Event | Pitcher or Filter Program | Sample | Flushing Instructions | Consumer Notification Template | Public Education |
| Full LSLR | Yes | Yes | Yes | Template 1 | Yes |
| Partial LSLR | Yes | Yes | Yes | Template 1 | Yes |
| Emergency LSLR | Yes | Yes | Yes | Template 1 | Yes |
| Customer notifies utility of intent to replace LSL in advance | Yes | No | Yes | Template 4 | Yes |
| Customer notifies utility of LSLR after completion | Yes | No | Yes | Template 4 | Yes |
| Disturbance of an LSL, GRR or Unknown Service Line | No | No | Yes | Template 2 | No |
| Disturbance of an LSL, GRR or Unknown Service Line from replacement of a water meter, meter setter, gooseneck, pigtail or connector | Yes | No | No | Template 3 | Yes |

Pitcher or Filter Requirements – The PWS must provide the consumer with a pitcher filter or point-of-use device certified by an American National Standards Institute (ANSI) accredited certifier to reduce Lead, six months of replacement cartridges, and instructions for use before the affected service line is returned to service. If the affected service line serves more than one residence or non-residential building (e.g., a multi-unit building), the PWS must provide a filter, six months of replacement cartridges and use instructions to every residence in the building.

Sample Requirements – The PWS must offer to collect a first draw follow-up tap sample between three months and six months after completion of a full or partial LSLR. The PWS must provide the results of the sample to the customer as soon as practicable, but no later than 3 calendar days after the PWS learns of the tap monitoring results. PWS must keep a copy of the laboratories sample results for their records for auditing purposes for 12 years as of the collection date of the samples.

Flushing Instructions – The PWS must provide information about service line flushing before the affected service line is returned to service. These instructions are for the customer to flush the service line and premise plumbing of particulate Lead.

Consumer Notification Templates -The PWS must notify customers of the risk of elevated Lead levels, provide public education materials, and provide flushing instructions before returning a service line to service following a replacement or disturbance. The templates address the required elements.

10. Lead Service Line Replacement Goal Rate (40 CFR § 141.84(d)(5-6))

LCRI requires all water systems to remove every Lead and GRR service line that is under their control (both public and private side) throughout the distribution system by December 31, 2037. This is accomplished by one of the following: - For the first 3 years (Nov. 1, 2027 to Dec. 31, 2030), water systems MUST replace Lead and GRR service lines (both public and private side) in their distribution system at a cumulative average annual replacement rate of at least a minimum 10% across this timeframe (will be determined on Dec. 31, 2030). - Beginning Jan. 1, 2031 to Dec. 31, 2037, the replacement rate becomes a minimum of 10% annually. - To calculate the cumulative average annual replacement rate, refer to EPA’s fact sheet found at: https://www.epa.gov/system/files/documents/2024-10/final_lcri_fact-sheet_calculating-service-line.pdf OR; - NDDEQ determines the system can replace all Lead and GRR service lines in less than the required 10 years. OR; - If eligible and approved by NDDEQ, water systems can use a deferred deadline. - For guidance determining eligibility, refer to EPA’s deferred deadline fact sheet: https://www.epa.gov/system/files/documents/2024-10/final_lcri_fact-sheet_deferred-deadlines.pdf

10a. Eligibility for Deferred Deadline for Lead Service Line Replacement (40 CFR141.84(d)(5)(vi)(A-C))

Check Eligibility and Document a Deferred Deadline for LSLR: - If eligible for a deferred deadline, the water system must: - Provide documentation of deferred deadline eligibility showing that 10% of known Lead and GRR service lines exceed 39 annual replacements per 1,000 service connections (unknowns are excluded). - Describe identification of the deferred deadline and associated cumulative average replacement rate that the water system considers to be the fastest feasible (but no slower than 39 replacements per 1,000 service connections), annual number of replacements required, duration, completion date, and plan to be reevaluated every 3 years. - NDDEQ requires the water system to provide information supporting the determination that annually replacing 10% of Lead and GRR service lines sooner and faster than 39 annual replacements per 1,000 service connections is not feasible. - Attach deferred deadline documentation to LSLR Plan

11.Annual Reporting Requirements for LSLR Plans

The PWS initial LSLR Plan must be submitted to NDDEQ prior to November 1, 2027 for approval - The PWS must submit annually an updated LSLR Plan or a notification stating there are no changes to the current LSLR Plan prior to January 30 of each year until all Lead, GRR and Lead connectors are removed, and all unknowns are identified. - LSLR Plan must be made publicly available by all PWS either in their PWS/city office or if it serves a population of 50,000 and greater, it must be posted online. - The LSLR Plan and all updates must be submitted to NDDEQ.

12. APPENDIX Check all that apply and are enclosed

☐ Appendix A: Instructions for customer flushing following a LSLR (40 CFR § 141.84(b)(5)) Templates 1-5

☐ Appendix B: Instruction for Flushing by Utility Immediately after LSLR

☐ Appendix C: NDDEQ Tracking Form-PWS Attempts to Contact Customers for LSLR (In development)

☐ Appendix D: NDDEQ Consumer Service Line Notification templates. (These templates can also be found at the following website: https://deq.nd.gov/mf/DWP/LCRR/ )

Appendix A

Instructions for customer flushing following a Lead service replacement

After a service line is replaced, the customer should flush all interior premise plumbing before using the water again. Subsequent flushing by the customer should be done once every two weeks for three months or at other intervals based on monitoring results if available. Utilities may want to encourage best times to flush based on water demand and operations (for example, when neighbors' water usage is low, e.g., midmorning to dinner time or late at night). Customers should be advised not to use hot water in the premise plumbing until initial flushing is completed to prevent sedimentation of Lead particles in premise hot water tanks.

Instructions for customers.

1. 	Find all the faucets that will drain, including the basement and all floors in your house.

2. 	Remove aerators and screens whenever possible, including the shower heads, from all faucets you plan to flush.

3. 	Include the laundry tubs, outdoor hose-bibs (spigots), bathtubs, and showers as flushing points.

4. 	After all the aerators are removed, open the faucets in the basement or on the lowest floor in the house. Leave all faucets running at highest rate possible, using cold water.

5. 	After the faucets are all open on the lowest floor, open the faucets on next highest floor of the house. Continue until faucets are open on all floors.

6. 	After all faucets are opened, leave the water running for at least 30 minutes.

7. 	After 30 minutes, turn off the first faucet you opened and continue to turn off other faucets in the same order you turned them on.

8. 	Clean aerators/screens at each faucet. You may need to replace aerators/screens if too old or worn. To clean aerators, cover the drain in your sink to prevent any aerator parts from falling into the drain, then unscrew the aerator and separate each part. Remove any small particles on the screen, soak the parts in white vinegar for a few minutes, and scrub the parts with a brush. After cleaning, put the aerator parts back together and screw the aerator back onto the faucet.

# Consumer Notice Template 1

# Full or Partial Lead Service Line Replacement

We completed a replacement, and we are required to provide this information.

[Name of PWS]

[Name and phone number for PWS point of contact]

Flush your service line prior to use

After a service line is replaced, the customer should flush all interior premise plumbing before using the water again. Subsequent flushing should be done once every two weeks for three months or at other intervals based on monitoring results if available. Do not use hot water in the premise plumbing until initial flushing is completed to prevent sedimentation of Lead particles in premise hot water tanks.

Instructions for customer flushing:

1. 	Find all the faucets that will drain, including in the basement and on all floors in your house.

2. 	Remove aerators and screens whenever possible, including the shower heads, from all faucets you plan to flush.

3. 	Include the laundry tubs, hose-bibs (spigots), bathtubs, and showers as flushing points.

4. 	After all the aerators are removed, open the faucets in the basement or on the lowest floor in the house. Leave all faucets running at highest rate possible, using cold water.

5. 	After the faucets are all open on the lowest floor, open the faucets on next highest floor of the house. Continue until faucets are open on all floors.

6. 	After all faucets are opened, leave the water running for at least 30 minutes.

7. 	After 30 minutes, turn off the first faucet you opened and continue to turn off other faucets in the same order you turned them on.

8. 	Clean aerators/screens at each faucet. You may need to replace aerators/screens if too old or worn. To clean aerators, cover the drain in your sink to prevent any aerator parts from falling into the drain, then unscrew the aerator and separate each part. Remove any small particles on the screen, soak the parts in white vinegar for a few minutes, and scrub the parts with a brush. After cleaning, put the aerator parts back together and screw the aerator back onto the faucet.

Filter

We are required to provide consumers with a pitcher filter or point-of-use device certified by an American National Standards Institute (ANSI) accredited certifier to reduce Lead, six months of replacement cartridges and instructions for use.

# Health effects of Lead

# There is no safe level of Lead in drinking water. Exposure to Lead in drinking water can cause serious health effects in all age groups, especially pregnant people, infants (both formula- fed and breastfed), and young children. Some of the health effects to infants and children include decreases in IQ and attention span. Lead exposure can also result in new or worsened learning and behavior problems. The children of persons who are exposed to Lead before or during pregnancy may be at increased risk of these harmful health effects. Adults have increased risks of heart disease, high blood pressure, kidney or nervous system problems. Contact your health care provider for more information about your risks.

Lead is a common metal that has been in many consumer products but is now known to be harmful to human health if ingested or inhaled. It can be found in Lead-based paint, air, soil, household dust, food, some types of pottery, and drinking water. Lead is rarely found in natural sources of water such as rivers, lakes, wells, or springs.

# Steps you can take to reduce exposure to Lead in drinking water:

- Run your water before use. Daily, allow the water to run at the tap for 5 minutes to flush water through the service line and plumbing in the house before using it for drinking or cooking. Taking a shower, running the dishwasher, or flushing the toilet will also flush your lines.

- Use cold water for drinking, cooking, and preparing baby formula. Do not cook with or drink water from the hot water tap as Lead dissolves more easily into hot water. Do not use water from the hot water tap to make baby formula.

- Clean your aerator. Regularly clean your faucet’s screen (also known as an aerator). Sediment, debris, and Lead particles can collect in your aerator. If Lead particles are caught in the aerator, Lead can get into your water.

- Do not boil water to remove Lead. Boiling water does not remove Lead.

- Obtain an NSF (National Sanitation Foundation) certified home water treatment device that is certified to remove Lead.

- Identify and replace plumbing fixtures containing Lead and any copper piping with Lead solder.

- Check home wiring. Water service lines are sometimes used to ground electrical lines. The wiring in your home or building may be attached to your water service line or elsewhere in your plumbing. If you have a Lead service line, this can accelerate its corrosion. Have a licensed electrician check your wiring.

- Get your child tested. Contact your local health department or healthcare provider to find out how you can get your child’s blood tested for Lead if you are concerned about exposure.

# Consumer Notice Template 2

# Disturbance to a Known or Potential Service Line Containing Lead

There was a disturbance to your service line

[Name of PWS]

[Name and phone number for PWS point of contact]

Potential for elevated Lead levels in drinking water.

Following a disturbance to your service line, such as operating a valve or changing your water meter, there is potential for elevated Lead levels in your drinking water. Please review the following information.

Flush your service line prior to use.

After a service line is disturbed, the customer should flush all interior premise plumbing before using the water again. Do not use hot water in the premise plumbing until initial flushing is completed to prevent sedimentation of Lead particles in premise hot water tanks.

Instructions for customer flushing:

1. 	Find all the faucets that will drain, including the basement and all floors in your house.

2. 	Remove aerators and screens whenever possible, including the shower heads, from all faucets you plan to flush.

3. 	Include the laundry tubs, hose-bibs (spigots), bathtubs, and showers as flushing points.

4. 	After all the aerators are removed, open the faucets in the basement or on the lowest floor in the house. Leave all faucets running at highest rate possible, using cold water.

5. 	After the faucets are all open on the lowest floor, open the faucets on next highest floor of the house. Continue until faucets are open on all floors.

6. 	After all faucets are opened, leave the water running for at least 30 minutes.

7. 	After 30 minutes, turn off the first faucet you opened and continue to turn off other faucets in the same order you turned them on.

8. 	Clean aerators/screens at each faucet. You may need to replace aerators/screens if too old or worn. To clean aerators, cover the drain in your sink to prevent any aerator parts from falling into the drain, then unscrew the aerator and separate each part. Remove any small particles on the screen, soak the parts in white vinegar for a few minutes, and scrub the parts with a brush. After cleaning, put the aerator parts back together and screw the aerator back onto the faucet.

Steps you can take to reduce exposure to Lead in drinking water:

- Run your water before use. Daily, allow the water to run at the tap for 5 minutes to flush water through the service line and plumbing in the house before using it for drinking or cooking. Taking a shower, running the dishwasher, or flushing the toilet will also flush your lines.

- Use cold water for drinking, cooking, and preparing baby formula. Do not cook with or drink water from the hot water tap as Lead dissolves more easily into hot water. Do not use water from the hot water tap to make baby formula.

- Clean your aerator. Regularly clean your faucet’s screen (also known as an aerator). Sediment, debris, and Lead particles can collect in your aerator. If Lead particles are caught in the aerator, Lead can get into your water.

- Do not boil water to remove Lead. Boiling water does not remove Lead.

- Obtain an NSF (National Sanitation Foundation) Certified home water treatment device that is certified to remove Lead.

- Identify and replace plumbing fixtures containing Lead and any copper piping with Lead solder.

- Check home wiring. Water service lines are sometimes used to ground electrical lines. The wiring in your home or building may be attached to your water service line or elsewhere in your plumbing. If you have a Lead service line, this can accelerate its corrosion. Have a licensed electrician check your wiring.

- Get your child tested. Contact your local health department or healthcare provider to find out how you can get your child’s blood tested for Lead if you are concerned about exposure.

# Consumer Notice Template 3

# Disturbance to a Known or Potential Service Line Containing Lead

There was a disturbance to your service line from replacement of a water meter, water meter setter, gooseneck, pigtail, or connector

[Name of PWS]

[Name and phone number for PWS point of contact]

Potential for elevated Lead levels in drinking water

Following a disturbance to your service line from replacement of a water meter, water meter setter, gooseneck, pigtail, or connector on the service line, there is potential for elevated Lead levels in your drinking water. Please review the following information.

Filters

We are required to provide consumers with a pitcher filter or point-of-use device certified by an American National Standards Institute (ANSI) accredited certifier to reduce Lead, six months of replacement cartridges and instructions for use.

# Health effects of Lead

# There is no safe level of Lead in drinking water. Exposure to Lead in drinking water can cause serious health effects in all age groups, especially pregnant people, infants (both formula- fed and breastfed), and young children. Some of the health effects to infants and children include decreases in IQ and attention span. Lead exposure can also result in new or worsened learning and behavior problems. The children of persons who are exposed to Lead before or during pregnancy may be at increased risk of these harmful health effects. Adults have increased risks of heart disease, high blood pressure, kidney or nervous system problems. Contact your health care provider for more information about your risks.

Lead is a common metal that has been in many consumer products but is now known to be harmful to human health if ingested or inhaled. It can be found in Lead-based paint, air, soil, household dust, food, some types of pottery, and drinking water. Lead is rarely found in natural sources of water such as rivers, lakes, wells, or springs.

Steps you can take to reduce exposure to Lead in drinking water

- Run your water before use. Daily, allow the water to run at the tap for 5 minutes to flush water through the service line and plumbing in the house before using it for drinking or cooking. Taking a shower, running the dishwasher, or flushing the toilet will also flush your lines.

- Use cold water for drinking, cooking, and preparing baby formula. Do not cook with or drink water from the hot water tap as Lead dissolves more easily into hot water. Do not use water from the hot water tap to make baby formula.

- Clean your aerator. Regularly clean your faucet’s screen (also known as an aerator). Sediment, debris, and Lead particles can collect in your aerator. If Lead particles are caught in the aerator, Lead can get into your water.

- Do not boil water to remove Lead. Boiling water does not remove Lead.

- Obtain an NSF (National Sanitation Foundation) Certified home water treatment device that is certified to remove Lead.

- Identify and replace plumbing fixtures containing Lead and any copper piping with Lead solder.

- Check home wiring. Water service lines are sometimes used to ground electrical lines. The wiring in your home or building may be attached to your water service line or elsewhere in your plumbing. If you have a Lead service line, this can accelerate its corrosion. Have a licensed electrician check your wiring.

- Get your child tested. Contact your local health department or healthcare provider to find out how you can get your child’s blood tested for Lead if you are concerned about exposure.

# Consumer Notice Template 4

# Customer Lead Service Line Replacement

Utility notified of intent to replace customer’s portion of an LSL.

Utility notified of completed replacement of customer’s portion of an LSL.

We are required to provide this information.

[Name of PWS]

[Name and phone number for PWS point of contact]

Flush your service line prior to use

After a service line is replaced, the customer should flush all interior premise plumbing before using the water again. Subsequent flushing should be done once every two weeks for three months or at other intervals based on monitoring results if available. Do not use hot water in the premise plumbing until initial flushing is completed to prevent sedimentation of Lead particles in premise hot water tanks.

Instructions for customer flushing:

1. 	Find all the faucets that will drain, including the basement and all floors in your house.

2. 	Remove aerators and screens whenever possible, including the shower heads, from all faucets you plan to flush.

3. 	Include the laundry tubs, hose-bibs (spigots), bathtubs, and showers as flushing points.

4. 	After all the aerators are removed, open the faucets in the basement or on the lowest floor in the house. Leave all faucets running at highest rate possible, using cold water.

5. 	After the faucets are all open on the lowest floor, open the faucets on next highest floor of the house. Continue until faucets are open on all floors.

6. 	After all faucets are opened, leave the water running for at least 30 minutes.

7. 	After 30 minutes, turn off the first faucet you opened and continue to turn off other faucets in the same order you turned them on.

8. 	Clean aerators/screens at each faucet. You may need to replace aerators/screens if too old or worn.

Filter

We are required to provide consumers with a pitcher filter or point-of-use device certified by an American National Standards Institute (ANSI) accredited certifier to reduce Lead, six months of replacement cartridges and instructions for use.

# Health effects of Lead

# There is no safe level of Lead in drinking water. Exposure to Lead in drinking water can cause serious health effects in all age groups, especially pregnant people, infants (both formula- fed and breastfed), and young children. Some of the health effects to infants and children include decreases in IQ and attention span. Lead exposure can also result in new or worsened learning and behavior problems. The children of persons who are exposed to Lead before or during pregnancy may be at increased risk of these harmful health effects. Adults have increased risks of heart disease, high blood pressure, kidney or nervous system problems. Contact your health care provider for more information about your risks.

Lead is a common metal that has been in many consumer products but is now known to be harmful to human health if ingested or inhaled. It can be found in Lead-based paint, air, soil, household dust, food, some types of pottery, and drinking water. Lead is rarely found in natural sources of water such as rivers, lakes, wells, or springs.

# Steps you can take to reduce exposure to Lead in drinking water

- Run your water before use. Daily, allow the water to run at the tap for 5 minutes to flush water through the service line and plumbing in the house before using it for drinking or cooking. Taking a shower, running the dishwasher, or flushing the toilet will also flush your lines.

- Use cold water for drinking, cooking, and preparing baby formula. Do not cook with or drink water from the hot water tap as Lead dissolves more easily into hot water. Do not use water from the hot water tap to make baby formula.

- Clean your aerator. Regularly clean your faucet’s screen (also known as an aerator). Sediment, debris, and Lead particles can collect in your aerator. If Lead particles are caught in the aerator, Lead can get into your water.

- Do not boil water to remove Lead. Boiling water does not remove Lead.

- Obtain an NSF (National Sanitation Foundation) Certified home water treatment device that is certified to remove Lead.

- Identify and replace plumbing fixtures containing Lead and any copper piping with Lead solder.

- Check home wiring. Water service lines are sometimes used to ground electrical lines. The wiring in your home or building may be attached to your water service line or elsewhere in your plumbing. If you have a Lead service line, this can accelerate its corrosion. Have a licensed electrician check your wiring.

- Get your child tested. Contact your local health department or healthcare provider to find out how you can get your child’s blood tested for Lead if you are concerned about exposure.

# Consumer Notice Template 5

# Planned Lead Service Line Replacement

We plan to replace your Lead service line, and we are required to provide this information.

[Name of PWS]

[Name and phone number for PWS point of contact]

Planned replacement date: [date]

[Use for partial service line replacement:]

Planned Partial Lead Service Line Replacement

We plan to partially replace a Lead service line (e.g., replace only the portion of a Lead service line owned by the water utility) in coordination with planned infrastructure work. We will replace the Lead service line from the water main to the water meter.

Notice Required

We must provide this notice to the owner of the affected service line, or the owner's authorized agent, as well as non-owner resident(s) served by the affected service line at least 45 days prior to the replacement.

# Health effects of Lead

# There is no safe level of Lead in drinking water. Exposure to Lead in drinking water can cause serious health effects in all age groups, especially pregnant people, infants (both formula- fed and breastfed), and young children. Some of the health effects to infants and children include decreases in IQ and attention span. Lead exposure can also result in new or worsened learning and behavior problems. The children of persons who are exposed to Lead before or during pregnancy may be at increased risk of these harmful health effects. Adults have increased risks of heart disease, high blood pressure, kidney or nervous system problems. Contact your health care provider for more information about your risks.

Lead is a common metal that has been in many consumer products but is now known to be harmful to human health if ingested or inhaled. It can be found in Lead-based paint, air, soil, household dust, food, some types of pottery, and drinking water. Lead is rarely found in natural sources of water such as rivers, lakes, wells, or springs.

Customer Portion of the Service Line

The customer or property owner is responsible for maintaining the portion of the service line from the water meter to the home or building (customer service line). As part of the planned infrastructure work, you may work with us to replace the customer service line at the same time as utility service line. The water utility is not required to bear the cost of replacement of the customer service line. Please contact us on the phone number above to learn more about replacement of the customer service line.

[Use for Full-Service Line Replacements:]

Planned Full Lead Service Line Replacement

We plan to complete a full replacement of a Lead service line (i.e., replace entire Lead service). We will replace the Lead service line from the water main to the home or building.

Notice Required

We must provide this notice to the owner of the affected service line, or the owner's authorized agent, as well as non-owner resident(s) served by the affected service line at least 45 days prior to the replacement.

# Health effects of Lead

# There is no safe level of Lead in drinking water. Exposure to Lead in drinking water can cause serious health effects in all age groups, especially pregnant people, infants (both formula- fed and breastfed), and young children. Some of the health effects to infants and children include decreases in IQ and attention span. Lead exposure can also result in new or worsened learning and behavior problems. The children of persons who are exposed to Lead before or during pregnancy may be at increased risk of these harmful health effects. Adults have increased risks of heart disease, high blood pressure, kidney or nervous system problems. Contact your health care provider for more information about your risks.

Lead is a common metal that has been in many consumer products but is now known to be harmful to human health if ingested or inhaled. It can be found in Lead-based paint, air, soil, household dust, food, some types of pottery, and drinking water. Lead is rarely found in natural sources of water such as rivers, lakes, wells, or springs.

Customer Portion of the Service Line

The customer or property owner is responsible for maintaining the portion of the service line from the water meter to the home or building (customer service line). Before proceeding with the work, we must establish an agreement. Please contact us on the phone number above to learn more about replacement of the customer service line.

Appendix B

Flushing by the utility/contractor immediately after Lead service replacement

After all connections have been completed, the utility will flush the water from an outside connection (such as hose-bib or hose leading from the house side of the meter installation) to remove any particles in the service line and near point-of-entry. The flushing is best done, if possible and practical, before the meter is connected in the service using a "jumper" or straight pipe in place of the meter. The straight pipe will allow for a higher velocity flush and protects the meter from potential damage from Lead pipe and other construction-related fragments. Flush at full velocity for at least 10 minutes. If the meter was replaced with a "jumper," it may be reconnected to the service after utility flushing. Following completion of flushing by the utility, the customer shall flush the interior premise plumbing as described in Appendix A.

Before the service line is returned to service, the water utility provides a copy of Appendix A, Instructions for Customer Flushing to the customer.

Appendix C

SERVICE LINE REPLACEMENT REFUSAL OR NON-RESPONSE FORM

In accordance with the LCRI, if a PWS identifies a LSL or GRR in any portion of the service line, including the private side, the line must be replaced, and the PWS must document the reasons why the replacement can’t be conducted. To ensure compliance, PWS are required to make at least four documented attempts using 2 different methods to complete the replacement. If a property owner refuses to permit the replacement of the private-side service line, or fails to respond after repeated attempts, the PWS must report the refusal or nonresponse to the NDDEQ. PWS must start collecting this information on November 1, 2027 and the reports are due to be submitted on January 30, 2029, and must be submitted every year thereafter.

FORM INSTRUCTIONS:

- Enter PWS Information

- Write the Public Water System (PWS) name and Identification Number (PWS ID).

- Provide Property Owner Details

- Add the owner’s full name.

- Include contact information (phone number, email).

- Fill in Address Information

- Record the street address, city, state, and ZIP code.

- If the service line serves multiple apartments, list only the building number.

- Specify the Purpose of the Form

- Indicate whether the form is being completed for an inspection attempt or a replacement attempt.

- Document Communication Attempts

- Record the date and time of each attempt.

- Note the form of communication (phone call, email, letter, in-person visit).

- PWS Representative Signature

- The representative completing the form must sign and date it.

- Repeat Required Attempts

- Complete the information for each attempt (form).

- At least four replacement attempts using two different methods must be documented.

- Submit the Form to NDDEQ

- After all four attempts have been completed and recorded, send the Service Line Inspection or Replacement Refusal Form to the North Dakota Department of Environmental Quality (NDDEQ) by January 30, 2029, and must be submitted every year thereafter.

- Mail to: NDDEQ, Div. of Municipal Facilities, 4201 Normandy Street, Bismarck, ND 58503-1324.

SERVICE LINE REPLACEMENT REFUSAL OR NON-RESPONSE FORM

§141.84(d)(3)

DETAILS

| Public Water System Name |  |
| --- | --- |
| PWS ID# |  |
| Property Owner’s Name |  |
| Contact Information |  |
| Address |  |
| Apartment/Building Number |  |
| City/ Town |  |
| The PWS identified a lead, galvanized (requiring replacement), or lead-status unknown service line at the property listed above. The property owner (pick one option below): |  |
| ☐ Failure to Respond/Non-Response | ☐ Refused Replacement |

ATTEMPT DOCUMENTATION

| Date | Time | Name of person (property owner) | Form of communication (email, letter, face-to-face, text, etc.) | Refused or Non-response | Print Name and Signature of the PWS personnel who made attempt |
| --- | --- | --- | --- | --- | --- |

CERTIFICATION OF NOTICE DISTRIBUTION

Signature of the PWS personnel___________________________________

Printed Name: ________________________________________________

Date: _______________________________________________________

# Appendix D

NDDEQ Consumer Service Line Material Type Notification Templates

These templates can be found at the following website:  https://deq.nd.gov/mf/DWP/LCRR/